PCS Platform 2022

نظام التحكم

Process Control System (PCS) for NLAP incineration plant

Platform System

Last update: Saturday, April 30, 2022

نظام التحكم بمحطة حرق النفايات وتوليد الطاقة عن طريق الحاسوب من خلال ال PLC

(Process Control system of station for waste incineration & Power generation by PLC & PC)

RPM Sensor

Contents

PCS Platform 2022	1

1	DELTA PLC	6

1.1	DELTA DVP20SX211R	6

1.2	Specifications	6

1.3	Product Profile	7

1.4	Point Specifications	7

1.4.1	Input point Specifications	7

1.4.2	Output point Specifications	8

1.4.3	Analog input & Analog output Specifications	8

1.5	Point Wiring	8

1.5.1	Input Point Wiring	8

1.5.2	Output Point Wiring	9

1.5.3	Analog input A/D & Analog output D/A External Wiring	10

1.6	DVP Slim Digital I/O Extension Unit	11

1.6.1	Model Numbers	11

1.6.2	Terminal layout	11

1.6.3	Input/Output points numbering order	11

1.7	DVP20SX2 Memory Map	13

1.8	PLC Device Address	15

1.9	Instructions	17

2	WPL Soft	18

2.1	الوصلة المخصصة لبرمجة ال PLC	18

2.2	كيفية انشاء برنامج لل PLC	18

2.3	خصائص تتعلق بتنزيل البرنامج على ال  PLC	19

2.4	تنزيل البرنامج عل ال PLC	20

2.5	مراقبة عمل ال PLC	20

3	Vijeo designer software	21

3.1	Create a new project	21

3.2	Selection of the communication protocol	22

3.3	Creating Variables	23

3.4	Create a Command Button	25

3.5	Create a Numeric Indicator	25

3.6	Create an alarm lamp	26

4	PLC Programing & wiring	27

4.1	Control Panel	27

4.2	تفعيل “Modbus Protocol” مع RS485 على ال PLC	28

4.3	التحكم في ضغط ال Boiler	29

4.3.1	توصيل “Pressure transmitter” مع ال PLC وبرمجته	29

4.3.2	توصيل “Atmospheric valve & Condenser valve”   مع ال PLC والتحكم بهم	32

4.4	نظام التحكم بال  Turbine	35

4.4.1	توصيل ال “Proximity Sensor” مع ال PLC وبرمجته	36

4.4.2	توصيل  محرك (single-phase motor) ال valve مع ال PLC والتحكم به	38

4.5	توصيل ال “Exhaust Fans” مع ال PLC والتحكم بهم من خلال الحاسوب (GUI)	43

4.5.1	طريقة توصيل ال fans مع ال PLC	43

4.5.2	التحكم ومراقبة ال Exhaust fans:	44

4.6	توصيل ال Supply Fans مع ال PLC والتحكم بهم من خلال الحاسوب (GUI)	44

4.6.1	طريقة توصيل ال fans مع ال PLC	45

4.6.2	التحكم ومراقبة ال Supply fans:	45

4.7	توصيل “Cooling pump” مع ال PLC والتحكم بها من خلال الحاسوب (GUI)	45

4.7.1	طريقة توصيل ال “Cooling pump” مع ال PLC	46

4.7.2	التحكم ومراقبة ال Cooling pump:	46

4.8	توصيل ال “Water pump”  مع ال PLC والتحكم بها من خلال الحاسوب (GUI)	46

4.8.1	طريقة توصيل ال “water pump 1̴ ” مع ال PLC	47

4.8.2	التحكم ومراقبة ال Water pump:	47

4.9	توصيل ال “Fuel burner” مع ال PLC والتحكم بها من خلال الحاسوب (GUI)	47

4.9.1	طريقة توصيل ال “Fuel burner” مع ال PLC	48

4.9.2	التحكم ومراقبة ال “Fuel burner”:	48

4.10	توصيل ال  “Electro filter panel” مع ال PLC و التحكم بها من خلال الحاسوب (GUI)	48

4.10.1	طريقة توصيل ال “Electro filer panel” مع ال PLC	49

4.10.2	التحكم ومراقبة ال “Electro filer panel”:	49

4.11	توصيل ال  “Condenser Water Tank Pump”مع PLC والتحكم بها من خلال الحاسوب (GUI)	49

4.11.1	طريقة توصيل ال “Condenser Pump” مع ال PLC	50

4.11.2	التحكم بال “Condenser Water Tank Pump”	50

4.12	توصيل ال  “Water Steam Cycle Main Pump (3phase)” و “Level Control Relay” مع ال PLC والتحكم بهم	50

4.12.1	طريقة توصيل “Level Control” مع ال PLC	51

4.12.2	مراقبة مستوى الماء في “Boiler tank” عن طريق ال PLC	52

4.12.3	توصيل “Water Steam Cycle Main Pump (3phase)” مع ال PLC	52

4.12.4	التحكم ومراقبة ال “Water Steam Cycle Main Pump (3phase)”	52

4.13	Electrofilter Current Monitoring	53

4.13.1	Connecting the Current Sensor to Controller	54

4.14	Boiler pressure control by  PLC & “Vijeo Designer”	65

4.14.1	Communication between Vijeo software and the PLC	65

4.14.2	Configure the communication settings	66

4.14.3	Create a Project in the Vijeo software for PC	66

4.14.4	Create Project in the WPL soft for PLC	68

4.14.5	Simulation	70

4.15	PLC Code	71

5	Graphical User Interface (GUI)	72

5.1	Introduction	72

5.2	Software Structure	73

5.2.1	Class diagram	73

5.2.2	Activity diagrams	73

5.2.3	Sequence diagrams	75

5.3	Pages	76

5.3.1	Overview	76

5.3.2	Other pages	77

5.3.3	Settings window	81

5.4	Use Instructions	81

5.5	Logger	82

5.6	Camera	82

5.6.1	Manually enter the address in VLC:	85

5.6.2	Use the script:	86

5.7	Appendix	87

5.7.1	Source code	87

5.7.2	Modbus connection	87

5.7.3	Development instructions	88

5.7.4	Camera manual	88

# DELTA PLC

## DELTA DVP20SX211R

## Specifications

_ Program capacity: 16k steps/Data register: 10k words

_ Higher execution speed compared to the competition: LD: 0.35μs, MOV: 3.4μs

_ Built-in mini-USB, RS-232 and RS-485 ports (Master/Slave) Supports standard

MODBUS ASCII/RTU protocol and PLC Link function

_ Supports real time clock for version 2.0 and above (no battery required) It operates for

at least one week after power off.

_Built-in 4 analog inputs / 2 analog outputs / 8 Digital Inputs & 6 Digital Outputs (Relay)

_ Supports DVP-S series left-side and right-side modules

_Power supply voltage: 24V DC

## Product Profile

## Point Specifications

### Input point Specifications

### Output point Specifications

### Analog input & Analog output Specifications

## Point Wiring

### Input Point Wiring

There are 2 types of DC inputs, SINK and SOURCE. (See the example below. For detailed point configuration, please refer to the specification of each model.)

### Output Point Wiring

Output terminals, Y0, Y1, and Y2, of relay models use C0 common port; Y3, Y4, and Y5 use C1 common port; as shown in the Figure. When output points are enabled, their corresponding indicators on the front panel will be on.

Relay (R) output circuit wiring

### Analog input A/D & Analog output D/A External Wiring

## DVP Slim Digital I/O Extension Unit

Model Explanation & Peripherals Thank you for choosing DVP-SS/SA/SX/SC series PLC. The 6~ 16 points extension offered by SS/SA/SX/SC series make the maximum digital I/O extension including the MPU reach 128 points. In addition, maximum 8 special modules (AD/DA/PT/TC/XA/RT) are extendable to DVP Slim series.

### Model Numbers

### Terminal layout

### Input/Output points numbering order

No matter how many points of MPU, the input of the first I/O extension unit will start from X20 and output will start from Y20.

Extension unit 3 DVP06SM11R will be used as 8 outputs, the higher 2 numbers of output points have no corresponding output points. Extension unit 4 DVP08SP11R will be used as 8 input points/8 output points, the higher part numbers of inputs points and output points have no corresponding input/output points. It is recommended to place them at the end of serial wiring, so that I/O points numbering will be continuous.

## DVP20SX2 Memory Map

## PLC Device Address

## Instructions

# WPL Soft

البرنامج المخصص لبرمجة ال PLC هو “WPL  Soft”

## الوصلة المخصصة لبرمجة ال PLC

نحتاج لوصلة UC-RRG020-12A مع التعريف من اجل توصيل الحاسوب بال PLC لبرمجتها.

RS232 ↔  USB

Dvp20sx2

Convertisseur sériel

UC-RRG020-12A

PC

## كيفية انشاء برنامج لل PLC

نضغط على  File – New

نختار نوع ال  PLC (ٍSX2)  ونضع اسم للمشروع في File Name ثم نضغط OK .

## خصائص تتعلق بتنزيل البرنامج على ال PLC

- بعد ربط الحاسوب بال PLC نضغط على RS232  في Communication setting على يسار البرنامج لتفقد وجود ال (COM4) Port لكي تتمكن من تنزيل البرنامج.

- يجب اختيارال address  station الخاص بال PLC (قبل استعمال ال PLC يكون ال address 1 ويمكن تغيره من خلال البرمجة) .

- يمكنا اختيار برمجة ال PLC اما ASCII او RTU .

## تنزيل البرنامج عل ال PLC

لتنزيل البرنامج نضغط الزر التالي

## مراقبة عمل ال PLC

لمراقبة عمل البرنامج في ال PLC نضغط على الز التالي

# Vijeo designer software

Vijeo Designer is a state-of-the-art software application with which you can create operator panels and configure operating parameters for human machine interface (HMI) devices. It provides all the tools needed to design an HMI project, from the data acquisition to the creation and display of animated drawings.

Realization of an application

The procedures to follow to implement an application are:

1- Create a new project,

2- Selection of the communication protocol.

3- Creating Variables

4- Create a Command Button

5- Create an alarm lamp.

6- Create a Numeric Indicator

## Create a new project

Create a new project, this dialog box appears when you start Vijeo Designer. Make sure Create new project is selected and click "Next" to continue.

Enter the name of your project and click Next. In our case, type "Manual".

Select the target type …, and the model ..., Click Next, Next.

## Selection of the communication protocol

Select the relevant driver for the device type using the Add button. Select “Schneider Electric Industrie SAS” as the Manufacturer, “ Modbus_(RTU)” as the driver, and “Modbus Equipment” as the Equipment. Then click on Finish.

## Creating Variables

A variable is a memory address indicated by a name. Vijeo Designer handles the following types of variables:

- BOOL

- INT (16 bit signed integer)

- UINT (16 bit unsigned integer)

- DINT (32 bit signed integer)

- UDINT (32 bit unsigned integer)

- Integer (1-32 bit generic integer)

- REAL

- STRING

- User Data Type (Array or Structure)

- Folder

- Block INT (16 bit signed block integer)

- Block UINT (16 bit unsigned block integer)

- Block DINT (32 bit signed block integer)

- Block Integer (1-32 bit generic block integer)

- Block REAL

Vijeo Designer uses the variables to communicate with devices. You can also define internal variables that will only be used by Vijeo Designer.

Right-click the "Variables" node in the "Navigator" window, select "New Variable" and click "BOOL".

Change the name of the Boolean-type "BOOL01" variable. In this window, specify the variable source (external in this case). In the Device Address property,

Right-click the "Variables" node in the "Navigator" window, select "New Variable" and click "Integer".

Change the name of the Boolean-type " Integer 01" variable to "High_level" in the Property Inspector. In this window, specify the variable source (external in this case). In the Device Address property,

## Create a Command Button

Select the "Switch" icon in the toolbar and draw an area on the panel where the button will be placed.

Select the "Switch" icon in the toolbar and use it to draw a rectangle, defining an area on the screen where it will be placed.

The Switch Settings window is displayed. Configure the properties as shown in the screen below:

In the General window:

- Select 00001 as the switch style.

Under the "When Touch" tab, click the icon         and:

- Select the "BOOL" "Emptying" variable,

- Select “Set” which will switch ON the Emptying bit when the button is pressed

- Click Add to confirm the selection.

Under the "When Release" tab, click the icon       and:

- select the "BOOL" "Emptying" variable,

- select “Reset” which will switch OFF the Emptying bit when the button is released

- Click Add to confirm the selection.

## Create a Numeric Indicator

Select the "Data Display" icon in the toolbar and draw an area on the screen where the numeric window will be placed.

The Numeric Display Settings window is displayed. Configure the properties as shown in the screen below:

In the "General" tab:

Click the icon            then:

double-click on the "Level" variable, then on OK in the expression editor,

To write in this indicator, Select the « Enable Input Mode » In the "Input mode" tab.

## Create an alarm lamp

The lamp animates depending on the state of the variable: red if it is active and green if it is inactive.

Select the "Lamp" icon in the toolbar and use it to draw a Lamp, defining an area on the screen where the lamp will be placed.

In this window, from the "General" tab:

Click the icon         then:

- Select the "BOOL" variable,

- Retain the lamp style 10001.

# PLC Programing & wiring

Delta PLC

Contactor1 for exhaust fan 1

Contactor2 for exhaust fan 2

Contactor3 for cooling pump

Contactor4 for water Pump pump

Relay1 for supply fans 1 & 2

Relay2 for Electro filter

Power supply 24 V DC

Blue Relay 1 & 2 for Valve

Contactor5 for exhaust fan 3

Relay3 for Fuel burner

Control Breaker

Power Breaker

Contacteur For Water Pump 3 phase

Level Control Relay

Control Panel

## تفعيل “Modbus Protocol” مع RS485 على ال PLC

الهدف من تفعيل “Modbus  Protocol” هو ربط ال PLC ب الحاسوب (GUI)

برنامج تفعيل “Modbus RTU slave” مع RS485 في ال PLC

M1002: Enable single positive pulse at the moment when RUN is activate (Normally OFF)

H81: Set up communication protocol as 9600, 8, N, 1

D1120: COM2 (RS-485) communication protocol

MOV H81 D1120: Set up communication protocol as 9600, 8, N, 1

SET M1143: For COM2 (RS-485), ASCII/RTU mode selection (OFF: ASCII; ON: RTU)

MOV K2 D1121: COM1 (RS-232) and COM2 (RS-485) PLC communication address 2 (K2= address 2)

MOV K100 D1129: COM2 (RS-485) Communication time-out setting (ms) (time k100=100ms)

SET M1120: Retaining the communication setting of COM2 (RS-485), modifying D1120 will be invalid when M1120 is set.

## التحكم في ضغط ال Boiler

(Boiler Pressure control)

Delta PLC 1

Pressur Sensor   Condenser   Atmospheric

Valve             Valve

نظام التحكم يكون عل الشكل التالي : أل PLC نقرأ ضغط البخار في Boiler من خلال  “Pressure sensor” وعند ارتفاع الضغط و بلوغ معدل “Condenser Pressure  Setpoint” مثلا 14.5bar تفتح “Condenser valve” لتخفيف البخار في Boiler وتحويله الى ال  Condenser  وعندما يرتفع الضغط اكثرفي ال Boiler ويبلغ معدل “Atmospheric Pressure  Setpoint”  مثلا 15 bar تفتح ال “Atmospheric valve”  لتفريغ من البخار في الهواء وعند انخفاض الضغط الى معدل “Min Pressure Setpoint” مثلا 14 bar فتغلق ال valve.

### توصيل “Pressure transmitter” مع ال PLC وبرمجته

#### مواصفات ال Pressure transmitter

COMPANY: GAMICOS

MODEL: GPT220

Range: 0-16bar

Output: 4-20 mA

Power: 12- 36V

Temperature: 2200 C

#### طريقة توصيل ال Sensor مع ال PLC

CH1

#### برنامج قراءة ضغط  الBoiler  في ال PLC

طريقة قراءة الضغط تكون عل الشكل التالي :

ال PLC تقرأ من Sensor (0 bar = 0 in PLC , 16bar =2000 in PLC)

لتحويل قراءة ال PLC الى قراءة شبيهة بالحساس نعمل ما يلي (   x×45مثلا 2000×45 =1600 ) نقرا قيمة الحساس من D1110 ونحفظها في D1 ثم نضرب 4 وتحفظ في D4 D3 ثم نقسم على 5 وتحفظ في D6 D5 على شكل شبيه بقيمة الحساس .

(0 bar = 0 in D5, 16bar =1600 in D5)

M1000: normal on

D1115: analog input/output mode setting

MOV K257 D1115: (257 decimal = 0000 0001 0000 0001 Binary),

Bit 0 = 1:  analog input mode of AD0 is the current mode

Bit 8 =1: current 4-20 mA.

D1110: analog input channel 0 (AD 0)

MOV D1110 D1: move D1110 in D1

MUL32 D1 K4 D3:

(D2, D1) × (4) = (D4, D3)

DIV32 D3 K5 D5:

(D4, D3) / (5) = (D6, D5)

### توصيل “Atmospheric valve & Condenser valve”   مع ال PLC والتحكم بهم

Atmospheric Solenoid valve    	Condenser Solenoid valve

#### طريقة توصيل ال “Atmospheric valve & Condenser valve” مع ال PLC

PhH

NH

Atm. Valve

Con. valve

#### برنامج التحكم ب “Atmospheric valve & Condenser valve”

يمكن التحكم بال  (Condenser valve) بشكل يدوي (Manual) عن طريق الحاسوب من خلال  Address M10 (ارسال  من الحاسوب بواسطة Modbus  “1” الى M10 فتعمل Y3 ON فيفتح ال valve او ارسال "0" الى M10 فتصبح Y3 OFF فيغلق ال valve   ) . يمكن ايضا التحكم بال  Atmospheric valve بشكل يدوي (Manual) عن طريق الحاسوب من خلال & M44 Address M11  فعند ارسال "1" الى M44 يتم تحويل التحكم الى يدوي ومن ثم ارسال “1” الى ال M11 فيتم تشغل Y4 فيفتح ال Valve  او ارسال "0" الى ال M11 فيتم فصل Y4 فيغلق ال  Valve  .

يمكن التحكم بال  “Condenser valve” بشكل اوتوماتيكي عن طريق ال  Pressure : فعند ارتفاع ال pressure  (في ال D5 )  وبلوغ معدل“ Condensor Pressure  Setpoint “ (في ال D8 وهو 950 اي 950 bar  والذي يمكن تعديله ) فتصبح  M0 ON والتي بدورها تشغل Y3 لتفتح ال valve. وعند انخفاض ال Pressure (في ال D5 )  وبلوغ معدل“Min Pressure  Setpoint” (في ال D7 وهو 800 اي 8 bar والذي يمكن تعديله ) فتصبح  M0 OFF والتي بدورها تفصل Y3 فتغلق ال valve.

عندما تكون “M44 OFF” (يتم التحكم بال M44 بواسطة الحاسوب) يمكن التحكم بال  “Atmospheric valve” بشكل اوتوماتيكي عن طريق ال  Pressure : فعند ارتفاع ال pressure (في ال D5 )  وبلوغ معدل “Atmospheric Pressure  Setpoint” (في ال D9 وهو 1000 اي 10 bar والذي يمكن تعديله ) فتصبح  M1 ON والتي بدورها تشغل Y4 لتفتح ال valve. وعند انخفاض ال Pressure (في ال D5 )  وبلوغ معدل“Min Pressure  Setpoint” (في ال D7 وهو800 اي 8 bar والذي يمكن تعديله ) فتصبح  M1 OFF والتي بدورها تفصل Y4 فتغلق ال valve.

يمكن السماح بتعديل ال Set point بشكل يدوي من خلال الحاسوب عن طريق ارسال"1"عن طرق ال Modbus الى address M12  او "0" لالغاء التعديل وابقاء Auto Setpoint.

يمكن السماح بتعديل ال Set point من الحاسوب ضمن حدود محددة في ال PLC ويجب ان يكون

ال “Atmospheric Pressure  Setpoint” هو الاعلى وان لا يتخطى ال 11 bar وان يزيد عل الاقل ب 0.3 bar  عن

ال “ Condensor Pressure  Setpoint “.

اما ال “ Condensor Pressure  Setpoint “ فيجب ان لا يتخطى “Atmospheric Pressure  Setpoint” وان يزيد عل الاقل ب 0.2 bar عن “Min Pressure  Setpoint”.

في ما يخص ال “Min Pressure  Setpoint” وهو الأدنى ويجب ان لا يتخطى ال “Condensor Pressure  Setpoint” وان لا ينخفض الى ما دون ال 7 bar.

## نظام التحكم بال  Turbine

(Turbine governing system)

Delta PLC 1

RPM Sensor    Turbine Valve

نظام التحكم يكون عل الشكل التالي : عند ارتفاع الضغط الى الحد المطلوب (مثلا 7 bar)  فيتم تشغيلM42  من خلال الحاسوب فيبدأ التحكم بفتح ال Turbine valve  ويدور ال Turbine من خلال البخار.

نقرأ بواسطة ال PLC سرعة ال Turbine من خلال RPM sensor فاذا كانت السرعة تعادل 1500 RPM فتبقى نسبة فتح ال Valve ثابتة واذ انخفضت السرعة الى ما دون ال 1500 فتعمل ال PLC عل زيادة نسبة فتح  ال  valve (زيادة نسبة فتح ال Valve يؤدي الي ذيادة البخارفيزيد من سرعة ال Turbine)  حتى نصل الى سرعة 1500, اما اذا تخطت السرعة  1500 فتعمل ال PLC عل تخفيض نسبة فتح ال Valve حتى نصل للسرعة المطلوبة.

### توصيل ال “Proximity Sensor” مع ال PLC وبرمجته

#### مواصفات ال “Proximity Sensor” وطريقة عمله

Proximity Sensor LJ12A3-4-Z/BX

قبل عمل الحساس يكون المفتاح مفتوح(Contact Normally opened)  وعند اقتراب مادة معدنية من الحساس يتغير الى مغلق.

#### طريقة توصيل ال Sensor مع ال PLC

Sensor	PLC

#### برنامج لاحتساب سرعة المولد في ال PLC

طريقة احتساب السرعة تكون عل الشكل التالي : في كل نصف دورة يلتقط “Proximity Sensor” اشارة فيتلقى X0 هذه الإشارة ويضاف 1 في ال  D20 ثم تتكرر العملية لمدة نصف ثانية من خلال العداد (T1) وخلال هذه المدة يتم تسجيل عدد الدورات في نصف الثانية  وتحفظ في D21 وعندما تنهي  المدة ON) (T1 نحصل عل السرعة في الدقيقة وتحفظ في ال D22 ويتم تصفير العداد (D0 & T1) لاحتساب السرعة من جديد.

-INCP D20: When X0 is triggered, the content of D20 will be incremented by 1.

-TMR T1 K15 : M1000 is ON, T1 is activated After 0,1 seconds (K5 × 0.1 sec = 0,5 sec), contact T1 is ON.

-When T1 is OFF move D20 in D21

-When T1 is ON : Multi D21 x 60 and move in D22; D20 is cleared & Reset T1

-When Reset T1 then the operation is repeated.

### توصيل  محرك (single-phase motor) ال valve مع ال PLC والتحكم به

#### طريقة ربط محرك الvalve   بال PLC

Relay1

PLC

Valve

Relay2

الRelay 1 لتشغيل المحرك وال Relay 2 لتغير الاتجاه (عند تشغيل Relay 2  فهذا يعني أن المحرك جاهز لإغلاق ال Valve وعند توقيف Relay 2 يعني ان المحرك مستعد لفتح ال Valve )  نقرأ نسبة الفتح او الاغلاق التي نفذت من خلال وجود ال Potentiometer (نحصل عل نسبة voltage من potentiometer عل حسب نسبة فتح ال valve).

Potentiometer

Voltage Out

Voltage In

A potentiometer is a manually adjustable, variable resistor with three terminals. Two terminals are connected to a resistive element, the third terminal is connected to an adjustable wiper. The position of the wiper determines the output voltage.

#### طريقة توصيل المحرك مع ال Relay

#### طريقة توصيل ال Relay وال potentiometer مع ال PLC

PhH

NH

A2

Relay1

Relay2

A1

A1

Voltage Out

Voltage In

R2

#### برنامج التحكم ب Valve في ال PLC

عندما يصبح  الضغط  في D5 حوالي 7 bar  نقوم بتشغيل  “M42 ON” من خلال الحاسوب لنبدأ التحكم بنسبة فتح ال “turbine valve”.

يتم تحديد نسبة فتح “turbine valve” من خلال ال PID في ال PLC او بشكل يدوي من خلال الحاسوب (GUI)

تعمل ال PID بمقارنة السرعة المطلوبة “Speed SetPoint” في D10 مع سرعة ال Turbine في D11 وتحدد نسبة المئوية المطلوبة لفتح ال Valve في D12 .

يكون التحكم بنسبة فتح ال valve المطلوبة بشكل اوتوماتيكي عندما تكون “M20 OFF” , فاذا كانت “M42 OFF” لا يسمح بفتح ال Valve اي نسبة الفتح صفر وتحفظ في D13 اما عندما “M42 ON” فيتم حفظ نسبة فتح ال Valve المطلوبة من PID في D13.

يمكن التحكم بنسبة فتح ال valve المطلوبة بشكل يدوي من خلال الحاسوب (GUI) ارسال "1" عن طريق ال Modbus الى  PLC-M20  فتصبح “M20 ON” ومن ثم نرسل النسبة المئوية لفتح ال valve الى D13 (اذا كان الرقم المرسل الى D13 اكثر من مئة يستبدل ب 100).

نغزي ال potentiometer ب10V من خلال DA0 (VO0) ونقرأ من ال potentiometer نسبة فتح ال  valve من خلال AD1 (V1+) وتحفظ في ال D30  )عندما يكون ال valve مغلق يعطينا ال  قيمةpotentiometer 1V (200 in PLC) وعند الفتح بشكل كامل يعطينا (1700 in PLC) 8.5V ) ثم نحول الرقم الى نسبة مئوية ويحفظ في D32

(D32 =Pot Value -20015) .

يتم تحويل نسبة المئوية لفتح ال Valve المطلوبة  الى رقم (بين ال 200 و ال 1700) وحفظه في D15

(D15 =D13×15+200 ) لنتمكن من مقارنته مع قيمة ال potentiometer .

اذا كانت قيمة ال Potentiometer اكبر من 200 ,تصبح “M40 ON” أي تسمح باغلاق ال Valve.

اما اذا كانت قيمة ال Potentiometer تعادل 200 ,تصبح “M40 OFF” أي لا تسمح باغلاق ال Valve.

اذا كانت قيمة ال Potentiometer اكبر من 1700 ,تصبح “M41 ON” أي تسمح بفتح ال Valve.

اما اذا كانت قيمة ال Potentiometer تعادل 1700 ,تصبح “M41 OFF” أي لا تسمح بفتح ال Valve.

(1% =15 in PLC; 4% =60 in PLC)

اذا كان الفارق بين نسبة فتح ال valve المطلوبة و قيمة ال Potentiometer, اكثر من  4% , يسمح بتحريك ال valve من خلال M60 للاغلاق وM61 للفتح, اما اذا كان الفارق اقل من 4% فلا يسمح بتحريكه.

عندما تكون قيمة فتح ال valve المطلوبة اكثر من قيمة ال Potentiometer بما يزيد عن 4% تصبح “M33 ON” فتفتح ال valve بواسطة Y0 حتى يصبح قيمة ال potentiometer تعادل القيمة المطلوبة بشرط ان يكون ال potentiometer اقل من 8,5V .

اما عندما تكون قيمة فتح ال valve المطلوبة اقل من قيمة ال Potentiometer بما يزيد عن 4% تصبح”Y1 ON” اي تم اختيار اتجاه الاغلاق . نقرأ حالة الاتجاه (Relay 2) من خلال ال “X7” فاذا كانت “Relay2 ON” تصبح  “M34 ON” فتغلق ال valve بواسطة  Y0 و Y1 بما يعادل القيمة المطلوبة بشرط أن يكون ال Potentiometer اكثر من 1V.

## توصيل ال “Exhaust Fans” مع ال PLC والتحكم بهم من خلال الحاسوب (GUI)

Exhaust Fan 3                       Exhaust Fan 2                               Exhaust Fan 1

الهدف من ال “Exhaust fans” هو شفط الدخان من المحرقة لذلك يتم تشغيل ال fans بشكل يدوي عن طريق الحاسوب عند بداية الحرق.

### طريقة توصيل ال fans مع ال PLC

A1

PhH

NH

C1

C1Contactor 1

C2

A2

A2

C5

A2

Contactor 1(C1) for Exhaust fan 1; Contactor 2 (C2) for Exhaust fan 2; Contactor 5 (C5) for Exhaust fan 3.

(PLC DELTA DVP20SX2)                         (DVP16SP (Extension Unit))

C5

C2

C1

EF3

EF2

EF1

### التحكم ومراقبة ال Exhaust fans:

يتم التحكم ومراقبة ال Exhaust fans بشكل يدوي عن طريق الحاسوب (User interface) بواسطة ال Modbus على الشكل التالي :

: Exhaust fan 1

التحكم  بال fan : ارسال "1"  من (PC) الى PLC-Y0,Extension يؤدي الى تشغيل ال Contactor 1 والذي بدوره يشغل ال fan.

اما ارسال "0" الى Y0,Extension يؤدي الى توقيف ال Contactor 1 والذي بدوره يفصل ال fan.

مراقبة حالة ال fan : عند تشغيل ال Contactor تصبح PLC-X0,Extension = “1” وهي تعني ان ال fan تعمل.

وعندما يكون ال Contactor مفصول فتكون ال X0,Extension = “0” وهي تعني ان ال fan لا تعمل.

Exhaust fan 2:

التحكم  بال fan : ارسال "1"  من (PC) الى PLC-Y1,Extension يؤدي الى تشغيل ال Contactor 2 والذي بدوره يشغل ال fan .

اما ارسال "0" الى Y1,Extension يؤدي الى توقيف ال Contactor 2 والذي بدوره يفصل ال fan.

مراقبة حالة ال fan : عند تشغيل ال Contactor تصبح PLC-X1,Extension = “1” وهي تعني ان ال fan تعمل.

وعندما يكون ال Contactor مفصول فتكون ال X1,Extension = “0” وهي تعني ان ال fan لا تعمل.

Exhaust fan 3:

التحكم  بال fan : ارسال "1"  من (PC) الى PLC-Y2 يؤدي الى تشغيل ال Contactor 5 والذي بدوره يشغل ال fan

اما ارسال "0" الى Y2 يؤدي الى توقيف ال Contactor 5 والذي بدوره يفصل ال fan.

مراقبة حالة ال fan : عند تشغيل ال Contactor تصبح PLC-X2 = “1” وهي تعني ان ال fan تعمل.

وعندما يكون ال Contactor مفصول فتكون ال X2 = “0” وهي تعني ان ال fan لا تعمل.

## توصيل ال Supply Fans مع ال PLC والتحكم بهم من خلال الحاسوب (GUI)

Supply fan 1                                           Supply fan 2

الهدف من ال “Supply fans” هو تزويد المحرقة بالهواء لاستمرار عملية الحرق, لذلك يتم تشغيل ال fans بشكل يدوي من خلال الحاسوب (GUI) عند بداية الحرق.

### طريقة توصيل ال fans مع ال PLC

(Relay1 for Supply fans)

(DVP16SP (Extension Unit))

A1

PhH

NH

R1

C1Contactor 1

A2

### التحكم ومراقبة ال Supply fans:

يتم التحكم ومراقبة ال Supply fans بشكل يدوي عن طريق الحاسوب (User interface) بواسطة ال Modbus على الشكل التالي :

التحكم  بال fan : ارسال "1"  من (PC) الى PLC-Y4,Extension يؤدي الى تشغيل ال Relay 1  والذي بدوره يشغل ال fans.

اما ارسال "0" الى Y4,Extension يؤدي الى توقيف ال Relay 1 والذي بدوره يفصل ال fans.

مراقبة حالة ال fans : عند تشغيل ال Relay تصبح PLC-X4,Extension = “1” وهي تعني ان ال fans تعمل.

وعندما يكون ال Relay مفصولة فتكون ال X4,Extension = “0” وهي تعني ان ال fans لا تعمل.

## توصيل “Cooling pump” مع ال PLC والتحكم بها من خلال الحاسوب (GUI)

الهدف من “Cooling pump” تزويد ال Condenser بالمياه لتبريد البخار لذلك يتم تشغيل ال Pump  بشكل يدوي بواسطة الحاسوب (GUI) عندما يفتح ال “Condenser valve” او “Turbine valve” .

### طريقة توصيل ال “Cooling pump” مع ال PLC

(Contactor 3 for cooling pump)

A1

PhH

NH

C3

C1Contactor 1

A2

(DVP16SP (Extension Unit))

C3

Cooling pump

### التحكم ومراقبة ال Cooling pump:

يتم التحكم ومراقبة ال Cooling pump  بشكل يدوي عن طريق الحاسوب (GUI) بواسطة ال Modbus على الشكل التالي:

التحكم  بال pump : ارسال "1"  من (PC) الى PLC-Y2,Extension يؤدي الى تشغيل ال Contactor3  والذي بدوره يشغل ال pump . اما ارسال "0" الى Y2,Extension يؤدي الى توقيف ال Contactor3 والذي بدوره يفصل ال pump.

مراقبة حالة ال pump : عند تشغيل ال Contactor تصبح PLC-X2,Extension = “1” وهي تعني ان ال pump تعمل. وعندما يكون ال Contactor مفصولة فتكون ال X2,Extension = “0” وهي تعني ان ال pump لا تعمل.

## توصيل ال “Water pump”  مع ال PLC والتحكم بها من خلال الحاسوب (GUI)

الهدف من “Water pump” هو ملأ خزان ال Boiler بالماء الى حدود “level-Max” لذلك يتم تشغيل ال pump بشكل يدوي من خلال الحاسوب (GUI)  قبل تشغيل المحطة.

### طريقة توصيل ال “water pump 1̴ ” مع ال PLC

(Contactor 4 for water pump 1̴ )

A1

PhH

NH

C4

C1Contactor 1

A2

(DVP16SP (Extension Unit))

C3

Water pump

### التحكم ومراقبة ال Water pump:

يتم التحكم ومراقبة ال Water pump  بشكل يدوي عن طريق الحاسوب (User interface) بواسطة ال Modbus على الشكل التالي:

التحكم  بال pump : ارسال "1"  من (PC) الى PLC-Y3,Extension يؤدي الى تشغيل ال Contactor4  والذي بدوره يشغل ال pump . اما ارسال "0" الى Y3,Extension يؤدي الى توقيف ال Contactor4 والذي بدوره يفصل ال pump.

مراقبة حالة ال pump : عند تشغيل ال Contactor تصبح PLC-X3,Extension = “1” وهي تعني ان ال pump تعمل. وعندما يكون ال Contactor مفصولة فتكون ال X3,Extension = “0” وهي تعني ان ال pump لا تعمل.

## توصيل ال “Fuel burner” مع ال PLC والتحكم بها من خلال الحاسوب (GUI)

الهدف من الحراق “Fuel burner” هوبدأ عملية الحرق من خلال تشعيل النفايات او تغذية عملية الحرق بالوقود لذلك يتم تشغيل الحراق بشكل يدوي عن طريق الحاسوب (GUI) لبدأ عملية الحرق او عند الحاجة لتغذية عملية الحرق.

### طريقة توصيل ال “Fuel burner” مع ال PLC

(Relay3 for Fuel burner)

A1

PhH

NH

R3

C1Contactor 1

A2

(DVP16SP (Extension Unit))

### التحكم ومراقبة ال “Fuel burner”:

(يجب ان نضغط عل الكباس الموجود عل الحراق لكي نستطيع التحكم به)

يتم التحكم ومراقبة ال “Fuel burner”  بشكل يدوي عن طريق الحاسوب (GUI) بواسطة ال Modbus على الشكل التالي:

التحكم  بال Fuel burner : ارسال "1"  من (PC) الى PLC-Y6,Extension يؤدي الى تشغيل ال Relay3  والذي بدوره يشغل ال Fuel burner. اما ارسال "0" الى Y6,Extension يؤدي الى توقيف ال Relay 3  والذي بدوره يفصل ال Fuel burner.

مراقبة حالة ال Fuel burner : عند تشغيل ال Relay تصبح PLC-X6,Extension = “1” وهي تعني ان ال Fuel burner موصول ليعمل.

وعندما تكون ال Relay مفصولة فتكون ال X6,Extension = “0” وهي تعني ان ال Fuel burner  مفصول ولا يعمل.

## توصيل ال  “Electro filter panel” مع ال PLC و التحكم بها من خلال الحاسوب (GUI)

الهدف من “Electro filer“ تنقية الهواء الذي يخرج من المحرقة لذلك يتم تشغيل “Electro filter panel” بشكل يدوي بواسطة الحاسوب (GUI) عند تشغيل المحرقة.

### طريقة توصيل ال “Electro filer panel” مع ال PLC

(Relay2 for “Electro filer panel”)

A1

PhH

NH

R2

A2

(DVP16SP (Extension Unit))

### التحكم ومراقبة ال “Electro filer panel”:

يتم التحكم ومراقبة ال “Electro filer panel”   بشكل يدوي عن طريق الحاسوب (User interface) بواسطة ال Modbus على الشكل التالي:

التحكم  بال “Electro filer panel”  : ارسال "1"  من (PC) الى PLC-Y7,Extension يؤدي الى تشغيل ال Relay2  والذي بدوره يشغل ال “Electro filer panel”.

اما ارسال "0" الى Y7,Extension يؤدي الى توقيف ال Relay 2  والذي بدوره يفصل ال

“Electro filer panel”.

مراقبة حالة ال “Electro filer panel”  : عند تشغيل ال Relay تصبح PLC-X7,Extension = “1” وهي تعني ان ال “Electro filer panel” موصول ليعمل.

وعندما يكون ال Relay مفصولة فتكون ال X7,Extension = “0” وهي تعني ان ال “Electro filer panel”  مفصول ولا يعمل.

## توصيل ال  “Condenser Water Tank Pump”مع PLC والتحكم بها من خلال الحاسوب (GUI)

### طريقة توصيل ال “Condenser Pump” مع ال PLC

PhH

NH

Pump

### التحكم بال “Condenser Water Tank Pump”

يتم التحكم بال  “Condenser pump” بشكل يدوي “Manual” عن طريق الحاسوب بواسطة ال Modbus من خلال  Address PLC-Y5 (عند ارسال  “1” الى  Y5 فتصبح Y5 ON فتعمل ال pump اما عند ارسال "0" الى Y5 فتصبح Y5 OFF فتفصل ال pump   ) .

## توصيل ال  “Water Steam Cycle Main Pump (3phase)” و “Level Control Relay” مع ال PLC والتحكم بهم

Water Steam Cycle Main Pump (3phase)

Level Control Relay (PNSA 230 100)

Level sensors

الهدف من Level Control معرفة خزان ال Boiler  اذا كان ممتلأ او فارغ  فاذا كان الخزان فارغ يتم تشغيل

ال  “Water Steam Cycle Main Pump (3phase)” بشكل اوتوماتيكي لملأ خزان ال Boiler بالماء حتى حدود Level-Max.

### طريقة توصيل “Level Control” مع ال PLC

Level sensor

PLC DELTA DVP20SX2

### مراقبة مستوى الماء في “Boiler tank” عن طريق ال PLC

عندما ينخفض الماء في الخزان الى ما دون level sensor – Min يصبح المفتاح ال Relay 1-3 موصول  وبالتاليPLC-X6=”1” وهي تعني ان الخزان فارغ.

وعندما يمتلأ الخزان الى حدود  level sensor – Max فيصبح المفتاح ال Relay 1-3 مفصول وبالتالي PLC-X6=”0” وهي تعني ان الخزان ممتلأ.

### توصيل “Water Steam Cycle Main Pump (3phase)” مع ال PLC

(DVP16SP-Extension Unit)

A1

PhH

NH

C

C1Contactor 1

A2

### التحكم ومراقبة ال “Water Steam Cycle Main Pump (3phase)”

يمكن التحكم بال  “Pump 3 ̴ ” بشكل اوتوماتيكي عن طريق ال  “Level Control ” : فعند انخفاض الماء في الخزان  تكونPLC-X6 =”1” فيصبح “PLC-Y5,Extension” ON فيعمل ال Contactor وتشتغل ال Pump .

اما عندما يمتلأ الخزان فيصبح PLC-X6 =”0” وبالتالي PLC-Y5,Extension” OFF فيفصل ال Contactor وتتوقف ال Pump .

يمكن التحكم بال  “Water Pump 3 ̴ ” بشكل يدوي عن طريق الحاسوب  “GUI” بواسطة ال Modbus : للتشغيل اليدوي يجب ان نرسل “1” الى PLC-M50 لكي نستطيع التحكم بال Pump ومن ثم ارسال "1" الى ال PLC-M51 فتصبح “PLC-Y5, Extension” ON فيعمل ال Contactor وتشتغل ال Pump او ارسال “0” الى ال PLC-M51 فيصبح PLC-Y5, Extension” OFF فيفصل ال Contactor وتتوقف ال Pump.

مراقبة حالة ال Pump 3 ̴

عند تشغيل ال Contactor تصبح PLC-X5,Extension = “1” وهي تعني ان ال “Pump” تعمل.

وعندما يكون ال Contactor مفصولة فتكون ال X5,Extension = “0” وهي تعني ان ال “Pump”  لا تعمل.

## Electrofilter Current Monitoring

The electrofilter uses a high voltage potential between 2 coductors that charges the light polluted gas coming from previous filtering stage (and thus generates a small current at the secondary) and makes them heavy. These heavy particles will then drop down and thus significantly reduce the total pollution coming from the station.

To ensure the functionality of the electrofilter, a non-invasive current sensor is used to measure the current at the primary of the HV transformer. The current sensor used is shown below which has a linear curve and the following specs:

Figure 1. YHDC Current Transformer

Table 1. YHDC SCT013-010 Specs

| Parameter | Value |
| --- | --- |
| Rated input | 0-10A |
| Rated output | -1 to 1V |
| Accuracy | ±1% |
| Linearity | ≤0.2% |
| Turns ratio | 1:1800 |
| Working voltage, frequency | 660V, 50-1KHz |

### Connecting the Current Sensor to Controller

The current sensor produces an output voltage between -1V and +1V which represents -10 A to +10A respectively. However, every controller accepts only positive analog numbers (0 – 5V in case of Arduino) and (-10V-10V in case of PLC), so an offset is a must. The below circuit in figure 2 is designed to offset the readings coming from the current sensor.

Figure 2. Current Sensor with Offset Schematic

R1 and R4 are used to divide the reference voltage by half. So, the voltage across the capacitor is:

|  | - VC=R4R1+R4×Vref=12×Vref | - (1) |
| --- | --- | --- |

If Vref=5V, the measurements from the current sensor will be offset by 2.5V. And thus, the output from the sensor will be between 1.5V and 3.5V. The reference voltage affects the selection of the burden resistor (R5) which is chosen according to:

|  | - RburdenΩ=Aref×n22×Ipmax | - (2) |
| --- | --- | --- |

Where:

- Aref: Reference voltage in V

- n: Current transformer number of turns (= 1800)

- Ipmax: Maximum primary current in A (= 10 A)

#### Extracting RMS Readings

The current sensor measures instantaneous current by converting the electrical field generated by the current passing through a conductor into voltage. The drawing below in Figure 3 shows the location of the current sensor in the real system. The CT is connected into the primary and the readings will be transformed to secondary by ideal transformer relation between the 2 windings as in equation (3) below.

Figure 3. System Diagram

|  | - V1V2=I2I1=n1n2 | - (3) |
| --- | --- | --- |

The procedure of extracting the current from the CT sensor is discussed in the flowchart below in figure 4.

Figure 4. Programming Flowchart

In order to calculate the RMS current (which follows equation (4) below) from instantaneous current measurements, the code is divided into 3 sections as seen above:

|  | - IRMS=Ical×VrefADCres1N0NCTanalog-Vanalogoffset2 | - (4) |
| --- | --- | --- |

- Loop 1: In this loop, 200 analog readings taken from the CT are subtracted from the offset value (Vref / 2) and are saved in an array.

- Loop 2: The values of the voltages in the previous loop (generated by the CT with an offset) are squared and integrated.

- Result: In this section of the code, the RMS value of the current is calculated by doing a square-root of the integrated square voltages (which are image of the current) and then multiplied by the conversion factor Ical= 0.1VA which is given in the datasheet of the YHDC SCT013-010 CT.

#### CT and Arduino Testing

Before connecting the CT to PLC, it was tested by Arduino to ensure its functionality. The circuit in figure 2 was connected with Vref was set to 5V, burden resistance was put to 50 ohms, and a load of 40 W (or 0.18 A) was tested. A commercial Ammeter was used to make sure the readings generated from the CT are correct.

As can be seen from the results below, the CT connected to an Arduino gave the exact same current reading as a commercial ammeter.

The Arduino code is listed below:

const unsigned int numReadings = 200; //samples to calculate Vrms.

int readingsVClamp[numReadings];    // samples of the sensor SCT-013-010

int readingsGND[numReadings];      // samples of the span

float SumSqGND = 0;

float SumSqVClamp = 0;

float total = 0;

int PinVClamp = A0;    // Sensor SCT-013-010

int PinVirtGND = A1;

void setup() {

Serial.begin(115200);

// initialize all the readings to 0:

for (int thisReading = 0; thisReading < numReadings; thisReading++) {

readingsVClamp[thisReading] = 0;

readingsGND[thisReading] = 0;

}

}

void loop() {

unsigned int i=0;

SumSqGND = 0;

SumSqVClamp = 0;

total = 0;

for (unsigned int i=0; i<numReadings; i++)

{

readingsVClamp[i] = analogRead(PinVClamp) - analogRead(PinVirtGND);

delay(1); //

}

//Calculate Vrms

for (unsigned int i=0; i<numReadings; i++)

{

SumSqVClamp = SumSqVClamp + sq((float)readingsVClamp[i]);

}

total = sqrt(SumSqVClamp/numReadings);

total= (total * 0.1);

Serial.println(String(total) + " A");

delay(500);

}

#### CT PLC

The connections of the current sensor and the PLC are shown in the diagram below:

Figure 5. CT with PLC Connections

#### Experiment 1 (Not Recommended)

- M1002: Enables a positive pulse at the start of the PLC.

- MOV k0 D2: Set D2 to 0 which describes the max value later.

- MOV k200 D60: Set D60 to 200 which corresponds to 1V analog input max sensor input200 bit ×10 V2000 bit.

- MOV k0 D61: Set D61 to 0 which corresponds to 0V analog input minimum sensor input.

- MOV k10000 D62: Set D62 to 10000 which corresponds to (1000 mV ×10AV) that represents the desired upper limit scaling for input.

- MOV k0 D63: Set D3 to 0 which corresponds to the lower limit scaling for input.

- M1000: Monitoring normally open contact (closes when the PLC runs).

- MOV D1112 D0: Move the current readings from the AD2 (Analog input 2) to D0.

- MUL D0 D0 D3: D3=D02

- SQR D3 D4: D4= D3

- SCLP D4 D60: Scale the square-rooted variable D4 to numbers between 0 and 10000.

- > D5 D2: if D5 is greater than D2 (D2 represents the max value), put the max value equal to D5.

And finally, the value stored in D5 should be divided by 11000 ×2≈11410 to get an estimated value of the RMS current.

#### Experiment 2 (Working Well)

- M1002: Single positive pulse at the start of the PLC.

- MOV k0 D50 (Init step): set the loop counter variable to 0. Used to count the integral loops. Necessary for taking several actions.

- MOV k0 D51 (Init step): Begin the integrator with 0. This will be used to accumulate the voltages generated from the current transducer.

- MOV k250 D52 (Init step): Number of loops. The RMS current will be calculated every 250 loops.

- M1011: 10 ms clock pulse (5 ms ON and 5 ms OFF).

- CNT C0 k1: Enables a counter to only count for a single shot (each 10 ms). It is used to schedule the current readings at 10 ms.

- If 10 ms passed (C0 counts 1) and the loop counter is still less than the number of loops:

- MOV D1112 D53: take a current measurement from AD2 and store it in D53.

- MUL D53 D53 D54: D54=D532. The squared values of the voltages generated from the current sensor are stored in D54.

- ADD D51 D54 D51: D51=D51+D54= D54. Nothing but an integration process.

- INC D50: Increment the loop timer by 1.

- RST C0: Reset the counter.

- If the loop counter is equal to the number of loops:

- DIV D51 D52 D55: D55=D51D52=integratornumber of loops.

- SQR D55 D56: D56=CurrentRMS= D55=integratorNumber of loops.

- MOV k0 D50: Clear the loop counter.

- MOV k0 D51: Clear the integrator.

The RMS current (D56) is the desired value to be read. It should be divided by 20 to have the full reading of the current. A typical result is shown below. The real RMS load current is approximately 0.2A. The RMS current calculated by the PLC is found to be 4 (k4). This number should be divided by 20 (10AV×10V2000 Bits=1A20 Bits) to give (4 bits ×1A20 Bits=0.2A).

## Boiler pressure control by  PLC & “Vijeo Designer”

PLC

Modbus RS 485 Network

Pressur Sensor

Condenser valve

Atmospheric Valve

يكون التحكم في ال valves بشكل اوتوماتيكي بواسطة ال PLC (عندما يرتفع الضغط الى 15 bar يفتح  Condenser valve وعندما ينخفض الضغط الى 14.1 bar يغلق valve . اما عندما يصل الضغط الى 15.5 bar فيفتح atmospheric valve وعندما ينخفض الضغط الى 14.1 bar فيغلق ال Valve .

### Communication between Vijeo software and the PLC

RS485 ↔ USB

Dvp20sx2

Convertisseur sériel

Ex9530

PC

لربط ال PLC مع برنامج ال Vijeo نحتاج لوصلة Ex9530 مع التعريف

### Configure the communication settings

The communication parameters are given in the following table:

| Item | Specification |
| --- | --- |
| Protocol | Modbus (RTU) |
| Port | COM2 |
| Slave address | 2 |
| Baud Rate | 9600 |
| Data bits | 8 |
| Parity | None |
| Stop bit | 1 |

Application development

In this application, the Vijeo software:

Read the status of atmospheric valve

Read the status of condenser valve

Manual Control of atmospheric valve

Manual Control of condenser valve

Monitoring the pressure

Write in the PLC default pressure for test

The Application Settings are given in the following table:

Parameter

| Device in PLC | The address in decimal | Function | Action |
| --- | --- | --- | --- |
| M4 | 02053 | Read | Status of atmospheric valve |
| M10 | 02059 | Write | Control of atmospheric valve |
| M11 | 2060 | Write | Control of condenser valve |
| Y3 | 01284 | Read | Status of condenser valve |
| D5 | 44102 | Read | Monitoring the pressure |
| D7 | 44104 | Write | Write the default pressure for test |

### Create a Project in the Vijeo software for PC

1) Creation of a new project and one chooses Modbus RTU Protocol

2) Creating variables

3) Creation of the supervision page.

4) Definition of the communication parameters in the "Driver configuration" and "Equipment Configuration" windows ((the communication parameters in the "IO Manager" node from the "Navigator" window).

### Create Project in the WPL soft for PLC

If the pressure >= 15 bar, M0 ON & if the pressure <=14.1 bar, M0 OFF

If the pressure >= 15,5 bar, M1 ON & if the pressure <=14.1 bar, M1 OFF

If M0 ON or M10 ON from User interface, Solenoid valve Open by Y3

If D11> 1500 (the PLC Read from potentiometer > 7.5V), M4 ON (status of valve is open).

If M1 ON (the pressure >= 15.5 bar) or M11 ON from User interface & D11<1600 (if the valve is incomplete opening) & Y1 OFF, M3 ON (the valve is open by Y0)

If M1 OFF (the pressure <=14.1 bar) & M11 OFF from User interface & D11>300 (if the valve is incomplete closure), Y1 ON & M2 ON (the valve is close by Y0 & Y1)

Note: For test we replaced D5 (real pressure) by D7 (default Pressure from user)

### Simulation

## PLC Code

Code repository:

https://drive.google.com/drive/u/2/folders/1VO8wV5U4CwCbguXImYD23Xg7q7eMTa73

PLC Ladder Code

# Graphical User Interface (GUI)

## Introduction

The graphical user interface (GUI) is used to monitor and control the power plant.

It is developed in C# using visual studio 2017.

The main task of the GUI is to initiate and monitor the plants, intervening from time to time. The main control has the control unit with their PLCs.

The PC running the GUI is connected with the Control Unit via Modbus RTU (see figure below) using a USB to Serial adapter (see figure below). To establish working connection drivers are necessary. For driver installation instructions and more information see Modbus-connection in the Appendix.

Most of the power plant is directly connected to the Control Unit and thus visible in the GUI and possibly also controllable. But a few things are not. Below the camera, which monitors the combustion chamber. More in the chapter camera.

In this document we will see how the GUI-Software is structured, what it can do, and how it's started and used. In addition, the source code is included in the appendix, as well as other instructions that are helpful in the further development.

## Software Structure

### Class diagram

### Activity diagrams

The following diagram shows a simplified view of how the state machine works

The following diagram shows how an GUI page works

### Sequence diagrams

The following diagram shows an controlling interaction example (names may differ from code):

## Pages

### Overview

In the overview the most values/states of sensors and actuators are monitored. The control of some actuators is also possible (supply fan, exhaust fans, Fuel burner, cooling pump, water pump & condenser pump).

Color indication for states (Text fields):

For supply fan, exhaust fans, water pump, cooling pump, Fuel Burner:

-RedFalse/OFF

-GreenTrue/ON

For atmospheric and condenser valves:

-Red CLOSE

-Green OPEN

Color indication for control commands (Buttons):

For supply fan, exhaust fans, fresh water pump, cooling pump, Fuel Burner & Condenser pump:

-RedFalse/OFF Command is send (the state field should also be red (OFF))

-GreenTrue/ON Command is send (the state field should also be green (ON))

IMPORTANT NOTE:

                - If the buttons have a different color than the statefields, that means something is wrong with the sensor or the actuator.

                - If the buttons don’t change the color by clicking, that means something is wrong with the connection.

From the overview you can reach the other pages by clicking on the respective buttons (left upper side).

### Other pages

#### Boiler pressure Control (BPC)

On this page, it’s possible to view states of and control the atmospheric valve, condenser valve, and pressure. It is also possible to set different pressure setpoints (which affects the automatic opening and closing of the valves).

##### 5.3.2.1.1 Valves

Color indication for states (Text fields):

For atmospheric and condenser valves:

-Red CLOSE

-Green OPEN

Control indications (Buttons):

By clicking the Buttons its possible to open the valves manually.

There can be 2 situations:

-

Thant means the valve is in AUTOMATIC mode. Clicking the button will open the valve manually and turn into MANUAL mode.

-

Thant means the valve is in MANUAL mode (and OPEN). The valve will never close until returning into AUTOMATIC mode. Clicking the button will return into AUTOMATIC mode.

IMPORTANT NOTE:

                - If the label under the button indicates the MANUAL (OPEN) mode and the valve state (textbox) is not green (TRUE/OPEN), that means something is wrong with the sensor or the actuator.

                - If the buttons and the labels among them don’t change by clicking, that means something is wrong with the connection.

##### 5.3.2.1.2Pressure

The current pressure is monitored in bar:

Considering the setpoints there are 2 modes:

                - AUTOMATIC: the auto/man checkbox is not checked and label indicates AUTOMATIC. In this mode its not possible to set any setpoint manually. The valves (if they are in automatic-mode) will be controlled depending on the default pressure-setpoints saved in the PLC. For more details, see the PLC documentation.

                - MANUAL: the auto/man checkbox is checked and label indicates MANUAL. In this mode its possible to set the setpoints manually. By writing a setpoint, the valves (if they are in automatic-mode) will be controlled depending on the written setpoints. For more details, see the PLC documentation.

#### Turbine governing system (TGS)

##### 5.3.2.2.1 Valve

The current valve opening is monitored in %:

For the valve control there are 2 modes:

                - AUTOMATIC: the auto/man checkbox is not checked and the label indicates AUTOMATIC. In this mode, it’s not possible to set the valve opening manually. The valve will be controlled automatically depending on the turbine-speed-setpoint saved in the PLC (the setpoint can be either the default value or a manually written value. See 3.2.2.2-Turbine speed). For more details, see the PLC documentation.

                - MANUAL: the auto/man checkbox is checked and the label indicates MANUAL. In this mode, it’s possible to control the valve manually by writing an opening % to the PLC. For more details, see the PLC documentation.

##### 5.3.2.2.2 Turbine speed

The current turbine speed is monitored in rpm:

#### Incinerator power control (IPC)

On this page it’s possible to view the state of and control:

Supply fan, exhaust fans, Fuel burner.

All works like in the overview. For more indications how to control or what the color indicate, see overview.

#### Level control (LC)

On this page it’s possible to view the state of and control:

Water Pump 1 phase, Water steam Cycle Pump 3 phase, and Boiler water level.

Color indication for states (Text fields):

For Water Pump 1 phase, Water steam Cycle Pump 3 phase:

-RedFalse/OFF

-GreenTrue/ON

For Boiler water level:

-RedLOW

-GreenHIGH

Color indication for control commands (Buttons):

For Water Pump 1 phase, Water steam Cycle Pump 3 phase:

-RedFalse/OFF Command is send (the state field should also be red (OFF))

-GreenTrue/ON Command is send (the state field should also be green (ON))

#### Filtering System (FS)

On this page, the state of the filtering actuators (compressor, compressor valve, and electrofilter) are shown. The “current“ tab shows the current passing through the electrofilter.  This section works as IPC section before.

### Settings window

This window appears after starting the GUI-program. Here some settings can be set.

Until the current version there is no settings.

## Use Instructions

To start the GUI double click on the binary executable 'ContSys.exe' in the release folder named 'release', or 'current release', or '<date>release', or 'release<date>'. Anyway, there must be a shortcut of the executable on the desktop (on the operation laptop).

Once ran, the the settings window must appear.

For information how to set settings and what they mean see Settings window.

After closing this window, you must be directed to the overview window.

From there, to operate see Overview in Pages.

## Logger

The logger records the read values of sensors and states. It writes them in a text file named CS_log.txt (may change) located in C:/ControlSystemData (may change). The file and directory are created automatically in case they do not exist.

Recording period: always when the values are read. (might change, see source code)

Current Version saves file at plain-text-file, so for further processing and analysis or visualization, the file content should be taken manually from the text-file.

Time format: DD.MM.YYYY HH:MM: SS. mS

Line format (maybe needed for parsing): time<tab><variable-name>:<tab><value><tab><next-variable-name>………

Recording example: (in real one record is listed in one single line)

For more details, look in the source-code in the Appendix.

## Camera

To keep the inside of the incinerator in look, an IP camera is put in front from the outside.

The camera is not integrated in the GUI-program. The camera is independently accessed per the local network.

For configurations enter the camera-ip address in the browser (ip: 192.168.1.64 username: admin pass: admin12345). There you can also view the stream.

Another and better way to stream is through the direct streaming address using a streaming software like VLC.

There are 2 ways:

### Manually enter the address in VLC:

Steps:

- open VLC media player

- copy the address: rtsp://admin:admin12345@192.168.1.64:554/Streaming/channels/101	(possible addresses are in the text file “camera addresses.txt” on the Desktop)

- paste it into VLC (Ctr+V) and press Enter (otherwise you can click on Media->open nwtwork stream and paste the link there)

### Use the script:

Steps:

- Double Click the script “camera.bat” on the Desktop

- VLC will open....

For more possibilities and configurations see the camera manual.

## Appendix

### Source code

Code repository:

| GUI (C#) Source Code | See https://drive.google.com/drive/u/2/folders/1VO8wV5U4CwCbguXImYD23Xg7q7eMTa73 |
| --- | --- |

### Modbus connection

For a good introduction and understanding of the Modbus protocol and addressing, the following webpage is useful:

#### RTU/ASCI

The Modbus protocol can be used in asci or in RTU mode. In which one is used depending on the PLC programming. Currently used in code: RTU.

To change that, change the variable ‘rtu_or_asci’ in StateMachine.cs.

#### Modbus driver

On Windows 7(like our NLAP-laptop), this adapter (Ex9530) needs a manual installation of the driver.

Driver name: Prolific USB-to-serial comm Port

Driver file:

Installation:

- Install the driver from the zip file

- Check in device manager and check connection in GUI. If all ok you are done

- Open device manager

- Right click on the new device (adapter must be connected) either in Ports (COM & LPT) or in unknown devices. -> update driver

- Choose the second field (choose from computer…)

- Choose the second field (pick from a list…)

- Double-click on the new-installed driver.

- Done (no more problem mark if there was one)

Com port must be set to “COM 2” (important because of the plc-programming):

- In device manager on the device:

- Right-click->properties

- In “Port settings” tap:

- Click on “advanced”

- Choose “COM2” from drop list in Com Port number.

- Ok->you are done

#### Modbus addresses

A List of all Modbus-addresses used are listen in the following excel List:

### Development instructions

To make the further development easier some checklists or protocols list the steps for adding/removing sensors/actuators and changing the GUI background.

### Camera manual

Search here for the current manual (model: -):

https://www.hikvision.com/en/support/document-center/user-manual/