Taizhou Tonhe Flow Control Co., Ltd

Contact：yoyo zhang  Email:tohe08@china-tonhe.com   
Skype:meizi2661   Mobile:+86-18957612187

URL：www.china-tonhe.com | www.tonheflow.com

Tonhe A20-T Series

MOTORIZED BALL VALVE

Technical Parameters

| Product size | □NPT/BSP 1/4" 3/8” 1/2” 3/4” 1” 1-1/4” (2-way brass/ss304 valve) □NPT/BSP 1/4” 3/8” 1/2” 3/4” 1” (3-way brass valve) (Optional ) |
| --- | --- |
| Maximum working pressure | 1.0MPa |
| Circulation medium | Fluid, air |
| Rated voltage | □DC3-6V □DC5V □DC12V □DC24V □DC9-35V □AC110-230V (Optional ) |
| Wiring control methods | □CR2-01 □CR2-02 □CR3-01 □CR3-02 □CR3-03 □CR3-04 □CR3-05 □CR4-01 □CR5-01 □CR5-02 □CR7-01 □CR7-02 □CR7-03 □CR7-04 （Optional） |
| Working current | ≤500mA |
| Open/close time | ≤5S |
| Life time | 70000 times |
| Valve Body material | □Brass □SS304/316 （Optional） |
| Actuator material | Engineering Plastics |
| Sealing material | FKM & PTFE |
| Actuator rotation | 90° |
| Max. torque force | 2 N.M |
| Cable Length | 0.5m |
| Environment temperature | -15℃～50℃ |
| Liquid temperature | 2℃～90℃(Brass valve) 2℃～140℃(SS304/316 valve) |
| Manual override | □Yes No（Optional） |
| Indicator | □Yes No （Optional） |
| Protection class | IP67 |
| Certificate | CE(LVD EMC),ROHS and SS304 valve passed NSF61-G |
| Company passed | Iso9001:2015 |

Wiring diagram

CR201 Wiring Diagram ( 2 wires control )

·RD connect with positive, the BK connect with negative, the valve closed, the actuator automatically power off after in place , the valve remains fully closed position .

·BK connect with positive, the RD connect with negative, the valve open, the actuator automatically power off after in place, the valve remains fully open position .

﹡Suitable Working Voltage: DC3-6v, DC5V, DC12V, DC24V

﹡Exceeding the working voltage is forbidden

CR202 Wiring Diagram ( 2 wires control – Power reset function)

·When SW is CLOSED, the valve OPEN, the actuator automatically power off after in place.

·When SW is OPEN, the valve CLOSED, the actuator automatically power off after in place.

﹡Suitable Working Voltage: AC/DC9-35V，AC/DC110V-230V

﹡Exceeding the working voltage is forbidden
Please Note A20 CR2 02 must need charge time >10 seconds for every time use

CR3 01 Wiring Diagram (3 wires control )

·RD & GR connect with positive, BK connect with negative

·When OPEN( RD) & SW connected , the valve open, the actuator automatically power off after in place , valve remains fully open position

·When CLOSE(GR) & SW connected, the valve closed, the actuator automatically power off after in place, valve remains fully closed position.

﹡Suitable Working Voltage: DC5V, DC12V, DC24V

﹡Exceeding the working voltage is forbidden





CR302 Wiring Diagram (3 wires control )

·RD connect with positive, the BK & GR connect with negative

·SW CLOSED, the valve OPEN, the actuator automatically power off after in place.

·SW OPEN, the valve CLOSED, the actuator automatically power off after in place.

﹡Suitable Working Voltage: DC7-35V

﹡Exceeding the working voltage is forbidden

CR3 03 Wiring Diagram (3 wires control)

·RD& GR connect with positive, the BK connect with negative。

·SW CLOSED, the valve OPEN,  the actuator automatically power off after in place

·SW OPEN, the valve CLOSED,  the actuator automatically power off after in place.

﹡Suitable Working Voltage: AC/DC9-35V, AC110-230V

﹡Exceeding the working voltage is forbidden

CR304 Wiring Diagram ( 3 wires control )

·RD & GR connected with positive, and the BK connected with negative

·When RD & SW connected, the valve closed, the actuator automatically power off after in place , remains fully closed position

·When GR & SW connected, the valve open, the actuator automatically power off after in place , remains fully open position.

﹡Suitable Working Voltage: DC5V, DC12V, DC24V

﹡Exceeding the working voltage is forbidden

CR305 Wiring Diagram ( 3 wires control – normally closed)

·RD& GR connect with positive, the BK connect with negative。

·SW CLOSED, the valve OPEN,  the actuator automatically power off after in place

·SW OPEN, the valve CLOSED,  the actuator automatically power off after in place.

﹡Suitable Working Voltage: AC/DC9-24V,AC110-230V

﹡Exceeding the working voltage is forbidden

CR306 Wiring Diagram ( 3 wires control – Power reset funtion)

·RD& GR connect with positive, the BK connect with negative
·SW CLOSED, the valve close,  the actuator automatically power off after in place
·SW OPEN, the valve open,  the actuator automatically power off after in place.
﹡Suitable Working Voltage: AC/DC9-24V，AC/DC110V-230V
﹡Exceeding the working voltage is forbidden

CR401 Wiring Diagram (4 wires control )

- RD & BK are connected to the power, GY& GR are connected to the controlled wiring.

- When the SW is closed , the valve open

- When the SW is open , the valve closed

*Suitable Working Voltage:AC110V-230V

CR501 Wiring diagram ( with feedback signal)

1.RD connect with positive, the BK connect with negative，the valve closed, the actuator automatically power off after in place .

2.BK connect with positive, the RD connect with negative，the valve open, the actuator automatically power off after in place .

3.GR & WT are connect when the valve open fully, YW & WT are connect when the valve closed fully

﹡Suitable Working Voltage:：DC3-6v, DC5V, DC12V, DC24V

﹡Exceeding the working voltage is forbidden!

CR502 Wiring diagram ( with feedback signal and Power reset funtion)

·When SW is closed , the valve open. the actuator automatically power off after in place

·When SW is open, the valve closed, the actuator automatically power off after in place

﹡GR & WT are connect when the valve open fully, YW & WT are connect when the valve closed fully

﹡Suitable Working Voltage: AC/DC9-35V，AC/DC110V-230V

﹡Exceeding the working voltage is forbidden

CR701 Wiring Diagram ( 7 wires control with feedback signal )

---RD connect with positive

---GR connect with SW and negative wiring

--- BK connect with negative wiring

---SW open. the valve open, and keeping fully open.

---SW closed. the valve closed, and keeping fully closed.

----BL & GY connect with the valve’s fully open signal wiring

--- YW & WT connect with the valve’s fully closed signal wiring.

﹡Suitable Working Voltage: DC7-35V (wide input range voltage)

﹡Exceeding the working voltage is forbidden

※ Feedback with load ability：

① The Max. off voltage: DC36V AC220V  ② The Max. off current: ≦0.4A

CR702 Wiring Diagram ( 7 wires control with feedback signal )

1.RD & GR connect with positive, the BK connect with negative

2. When RD & SW connected, the valve open, the actuator automatically power off after the valve fully open.

3. When GR & SW connected, the valve closed, the actuator automatically power off after the valve fully closed,.

4. BL & GY connect with the valve’s fully open signal wiring

5. YW & WT connect with the valve’s fully closed signal wiring

﹡Suitable Working Voltage: DC5V, DC12V, DC24

﹡Exceeding the working voltage is forbidden

※ Feedback with load ability：

① The Max. off voltage: DC36V AC220V  ② The Max. off current: ≦0.4A

CR703 Wiring Diagram ( 7 wires control with feedback signal )

·RD& GR connect with positive, the BK connect with negative。

·SW CLOSED, the valve OPEN,  the actuator automatically power off after in place

·SW OPEN, the valve CLOSED,  the actuator automatically power off after in place.

·BL & GY connect with the valve’s fully open signal wiring

·YW & WT connect with the valve’s fully closed signal wiring.

﹡Suitable Working Voltage: AC/DC9-35V AC110-230v

﹡Exceeding the working voltage is forbidden

※ Feedback with load ability：

① The Max. off voltage: DC36V AC220V  ② The Max. off current: ≦0.4A

CR704 Wiring Diagram ( 7 wires control with feedback signal )

·RD & BK are connected to the power, GR & BL are connected to the controlled wiring.

·When the SW is closed , the valve open

·When the SW is open , the valve closed

·GR & WT connect with the valve’s fully open signal wiring

·YW & WT connect with the valve’s fully closed signal wiring.

Suitable Working Voltage:：AC/DC110V-230V

﹡Exceeding the working voltage is forbidden

CR705 Wiring Diagram ( 7 wires control with feedback signal,when power off valve closed itself )

.RD & GR connect with positive, BK connect with negative,
.SW closed valve open, actuator automatically power off after in place.
.SW open valve closed, actuator automatically power off after in place.
.When external power off, valve close,actuator automatically power off after in place.
.BL & GY connect with valve’s fully open signal wiring.
.YW & WT connect with valve’s fully open signal wiring.
.Suitable working voltage:AC/DC9-24V, AC110-230V
.Exceeding the working voltage is forbidden.

CR706 Wiring Diagram ( 7 wires control with feedback signal,when power off valve closed itself )

.RD & GR connect with positive, BK connect with negative,
.SW closed valve open, actuator automatically power off after in place.
.SW open valve closed, actuator automatically power off after in place.
.When external power off, valve open,actuator automatically power off after in place.
.BL & GY connect with valve’s fully open signal wiring.
.YW & WT connect with valve’s fully open signal wiring.
.Suitable working voltage:AC/DC9-24V, AC110-230V
.Exceeding the working voltage is forbidden.

Instruction For Manual Function

从全关到全开，手动要转七圈
motorized valve from full close to full open(S-O), the manual override need 7 turns